Three Phase Symmetry test

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location | Parent Location | Facility Area | Rated Line Voltage (V) | Voltage-L1L2 (V) | Voltage-L2L3 (V) | Voltage-L3L1 (V) | Voltage-L1N (V) | Voltage-L2N (V) | Voltage-L3N (V) | Average Line Voltage (V) | Average Phase Voltage (V) | Voltage Unbalance % | Rated Phase Current (A) | Current-L1 (A) | Current-L2 (A) | Current-L3 (A) | Average Phase Current (A) | Current Unbalance % | Voltage-NE (V) | Zero Sum Current (mA) | Current Result | NEV Result | ZeroSum Result |
| Main ACB | MLTP 1 | LT Panel Room | 415.0 | 425.0 | 420.0 | 415.0 | 243.0 | 245.187 | 240.813 | 420.0 | 243.0 | 0.9 | 630.0 | 508.713 | 458.3 | 407.487 | 458.3 | 11.0 | 3.7 | 156.0 | FAIL | FAIL | FAIL |